**PART 1 GENERAL**

1.01 GENERAL REQUIREMENTS

1. Provide all materials, labor, equipment and services necessary to furnish, deliver and install all work under this section as shown on the contract documents, specified herein, and as specified by the job conditions.

1.02 DESCRIPTION

1. Related work specified elsewhere:

1. Metal Fabrication. Section 05 50 00

2. Rough Carpentry. Section 06 10 00

3. Access Panels & Doors: Section 08 31 00

4. Painting: Section 09 91 00

5. Electrical: Division 26

1.03 SUBMITTALS

1. Procedures: Furnish submittals in accordance with the general requirements specified.
2. Shop Drawing: Furnish shop drawings for architect's approval. Include elevations, sections, and details indicating dimensions, materials, finishes, conditions for anchorage and support of each shutter.
3. Certifications: Submit manufacturer’s Underwriters Laboratories (UL), Warnock Hersey (WH) or Factory Mutual Research (FM) laboratory test report verifying product compliance in accordance with the required fire and smoke ratings.
4. Product Literature: Submit manufacturer's technical literature describing the product to be used under this section.
5. Maintenance and Operating Manuals: Furnish complete manuals describing the materials, devices and procedures to be followed in operating and maintaining all shutters under this section. Include manufacturer's brochures and parts lists describing the actual materials used in the product.

1.04 QUALITY ASSURANCE

1. Fire & Smoke Rated Assemblies: Provide all shutters with fire and smoke resistance rating required to comply with governing regulations which are inspected, tested, listed and labeled by UL, WH or FM and complying with NFPA 80 for class of opening. Provide units tested in accordance with the requirements of UL 10B, UL 1784, NFPA 252, ASTM E-152. Provide testing laboratory label permanently fastened to each fire and smoke shutter assembly.
2. Regulatory Requirements: Comply with applicable requirements of the laws, codes, ordinances and regulations of federal, state and municipal authorities having jurisdiction.
3. Manufacturer Requirements: Shutter manufacturer shall have been in the business of and have experience in manufacturing the type of product covered under this specification section as well as giving credible service for a minimum of five (5) years. Provide list of at least ten (10) completed projects which include the products covered under this section.

1.05 DELIVERY, STORAGE AND HANDLING

1. General: Deliver and store materials in manufacturer's original packaging, labeled to show name, brand and type. Store materials in a protected dry location off the ground in accordance with manufacturer's instructions.

1.06 WARRANTY

1. Shutter Warranty: Furnish one (1) year written warranty signed by the manufacturer and installer agreeing to repair or replace work which has failed as a result of defects in materials or workmanship. Upon notification within the warranty period, such defects shall be repaired at no cost to the owner.

**PART 2 PRODUCTS**

* 1. COILING COUNTER FIRE & SMOKE RATED SHUTTERS

1. Manufacturer: Coiling counter fire and smoke rated shutters shall be Auto-Set System model CFS-HK-G as manufactured by McKeon Door Company.
   1. MATERIALS
2. Curtain: Shall be assembled of interlocking galvanized steel slats, cold rolled. Slats shall have endlocks locking each end of alternate slats to act as a wearing surface, and maintain slat alignment. Curtain shall be 22 gauge minimum or gauge required by UL, WH or FM which ever is greater.
   1. Slats: Shall be of a cross section not less than 1¼" wide by ½" deep.
3. Bottom Bar: Shall consist of a single steel angle not less than 1½” x 1½” formed to fit slats. Bottom bar shall be provided with slotted holes to allow for thermal expansion.
4. Guides: Each guide assembly shall be fabricated of a minimum 1/8” steel angles and channels formed to a box type configuration. Guides shall be provided with slotted holes to allow for thermal expansion.
   1. Provide internal, fully concealed UL Classified smoke seals located within each guide assembly. Externally mounted smoke seals shall not be acceptable.
   2. Drywall Applications: Provide steel support tubes designed and constructed with a slip joint at the top to allow for thermal expansion.
5. Mounting Brackets: Fabricated of hot rolled 1/8” steel plate minimum, brackets shall be provided to house ends of the counterbalance barrel assembly.
6. Hood: Shall be provided to entirely enclose curtain and counterbalance barrel assembly. Hood shall be fabricated 22 gauge galvanized steel and designed to match brackets. Top and bottom shall be bent and reinforced for stiffness.
   1. Provide UL Classified lintel smoke seals.
7. Counterbalance Assembly: Fire shutter shall be counterbalanced by means of adjustable steel helical torsion springs attached to shaft enclosed in pipe with required mounting blocks or rings for attachment of curtain. Grease sealed bearings or self-lubricating graphite bearings shall be attached to the spring barrel which shall be fabricated of hot formed structural quality carbon steel seamless pipe.
8. Hand Crank Operator: Fire shutter shall be provided with a compact reduction geared unit designed and built by the shutter manufacturer. High efficiency reduction gearing running in an oil bath, shall be furnished together with a centrifugal governor and a fail-safe magnetic release device, completely housed to protect against damage, dust and moisture.
9. Self-Closing Mechanism: The fire shutter is to be designed with a centrifugal governor as an integral part of the operator's construction. The automatic release mechanism shall be activated by a fusible link, smoke detector or fire alarm. When activated the shutter is released and begins to close due to gravitational force. The speed of the shutter is governed by a centrifugal governor at a rate of not greater than 9" per second or less than 6" per second.
10. Magnetic Release with 10 Second Time Delay: A fail-safe magnetic release device shall be built into the operator as an integral part of the release mechanism. When power is interrupted to the release mechanism by the smoke detector or fire alarm, the shutter shall begin to self-close. In the event of power failure the time delay shall prevent the fire shutter from closing for a period of 10 seconds. Once the 10 seconds have lapsed, the fire shutter shall self-close.
11. Easy Trip Test Feature: The fire shutter shall be designed so that it may be trip-tested simply activating the magnetic release device. By activating the magnetic release device, the shutter shall self-close. Once the fire shutter has satisfactorily closed, it shall be simply reset by pulling the reset cable. No ladders or tools shall be needed to reset the shutter or the magnetic release mechanism.
12. Finish: After completion of fabrication, clean all metal surfaces to remove dirt and chemically treat to provide for paint adhesion. Curtain assembly is to receive a prime coat finish of .2 mils of epoxy primer and .8 mils of polyester paint in a McKeon Sterling Gray finish.

**PART 3 EXECUTION**

3.01 EXAMINATION

1. Examine surfaces and field conditions to which this work is to be performed and notify architect if conditions of surfaces exist which are detrimental to proper installation and timely completion of work.
2. Verify all dimensions taken at job site affecting the work. Notify the architect in any instance where dimensions vary.
3. Coordinate and schedule work under this section with work of other sections so as not to delay job progress.

3.02 INSTALLATION

1. Perform installation using only factory approved and certified representatives of the shutter manufacturer.
2. Install shutter assemblies at locations shown in perfect alignment and elevation, plumb, level, straight and true.
3. Adjust shutter installation to provide uniform clearances and smooth non-binding operation.
4. Install wiring in accordance with applicable local codes and the National Electrical Code Standard. Materials shall be UL listed.
5. Test shutter closing sequence when activated by the building's fire alarm system. Reset shutter after successful test.

3.03 PROTECTION AND CLEANING

1. Protect installed work using adequate and suitable means during and after installation until accepted by owner.
2. Remove, repair or replace materials which have been damaged in any way.
3. Clean surfaces of grime and dirt using acceptable and recommended means and methods.