**PART 1 GENERAL**

1.01 GENERAL REQUIREMENTS

A. Provide all materials, labor, equipment and services necessary to furnish, deliver and install all work under this section as shown on the contract documents, specified herein, and as specified by the job conditions.

1.02 DESCRIPTION

A. Related work specified elsewhere:

1. Metal Fabrication. Section 05 50 00

2. Rough Carpentry. Section 06 10 00

3. Access Panels & Doors: Section 08 31 00

4. Painting: Section 09 91 00

5. Electrical: Division 26

1.03 SUBMITTALS

1. Procedures: Furnish submittals in accordance with the general requirements specified.
2. Shop Drawing: Furnish shop drawings for architect's approval. Include elevations, sections, and details indicating dimensions, materials, finishes, conditions for anchorage and support of each door.
3. Certifications:
   1. Submit manufacturer’s Underwriters Laboratories (UL), Warnock Hersey (WH) or Factory Mutual Research (FM) laboratory test report verifying product compliance in accordance with the required fire and smoke ratings.
   2. Provide manufacturer’s ICC Evaluation Service report confirming compliance of the fire door assembly in accordance with the requirements of the Building Code.
4. Product Literature: Submit manufacturer's technical literature describing the product to be used under this section.
5. Maintenance and Operating Manuals: Furnish complete manuals describing the materials, devices and procedures to be followed in operating and maintaining all doors under this section. Include manufacturer's brochures and parts lists describing the actual materials used in the product.

1.04 QUALITY ASSURANCE

1. Fire & Smoke Rated Assemblies: Provide all doors with fire and smoke resistance rating required to comply with governing regulations which are inspected, tested, listed and labeled by UL, WH or FM and complying with NFPA 80 for class of opening. Provide units tested in accordance with the requirements of UL 10B, UL 1784, NFPA 252, ASTM E-152. Provide testing laboratory label permanently fastened to each fire and smoke door assembly.
2. Regulatory Requirements:
   1. Comply with applicable requirements of the laws, codes, ordinances and regulations of federal, state and municipal authorities having jurisdiction.
   2. Listed by the ICC Evaluation Service in accordance with the applicable sections of the Building Code.
3. Testing: Provide documentation from a certified testing agency that the fire door’s self-closing governor mechanism and fire door operator have been tested for a minimum of 50,000 cycles and 500 self closing trip tests.
4. Manufacturer Requirements: Door manufacturer shall have been in the business of and have experience in manufacturing the type of product covered under this specification section as well as giving credible service for a minimum of five (5) years. Provide list of at least ten (10) completed projects which include the products covered under this section.

1.05 DELIVERY, STORAGE AND HANDLING

A. General: Deliver and store materials in manufacturer's original packaging, labeled to show name, brand and type. Store materials in a protected dry location off the ground in accordance with manufacturer's instructions.

1.06 WARRANTY

1. Door Warranty: Furnish one (1) year written warranty signed by the manufacturer and installer agreeing to repair or replace work which has failed as a result of defects in materials or workmanship. Upon notification within the warranty period, such defects shall be repaired at no cost to the owner.

**PART 2 PRODUCTS**

* 1. SIDE ACTING FIRE & SMOKE RATED DOORS WITH INTEGRAL EGRESS DOOR

1. Manufacturer: Side acting fire and smoke rated doors with integral egress door shall be the Safescape model S7700-SS as manufactured by McKeon Door Company.
   1. MATERIALS
2. General: Each unit shall consist of an interlocking slat curtain designed to travel in a horizontal plane, smoothly and without binding. Curtain shall be driven to the open and closed position by a positive action sprocket and integral endless drive chain system.
3. Curtain: Shall be fabricated of interlocking, stainless steel slats with an approximate cross section not less than 3" wide by 7/8" deep.
4. Leading Edge: Curtain shall be furnished with a stainless steel member of tubular design to provide stiffness, limit deflection and provide for a tight fitting closure.
5. Receiving Edge: Shall be fabricated of a stainless steel member with sufficient depth, designed to accept the leading edge and form a tight fitting closure when the door is the fully closed position.
6. Swinging Egress Door: Incorporated within the curtain shall be a swinging type stainless steel door designed and built as an integral part of the fire door's assembly.

1. Door Frame: Shall be a stainless steel unit, 14 gauge with the same labeled fire resistance rating as specified for door.

2. Door Assembly: Complete with door, hinge, and locking channel mechanism. 20 gauge stretcher leveled, stainless steel faces.

3. Hardware:

a. Fire Exit Device: Flush mounted integral type fire exit device on one face and with pull handle on opposite face of the swinging door.

b. Closer: Shall be concealed type.

1. Head Track: Shall be of not less than 1/8" thick stainless steel and shall be provided with an integral locking bar. The faying surface shall not be less than 38% of the flat plate area when the door is in the closed position. Locking bar shall lock and retain the curtain in place.
2. Floor Track (Optional): Shall be no greater than 1½” deep and include integral removable stainless steel protective cover plates to allow for easy cleaning and proper maintenance.
3. Perimeter Smoke Seals: Provide internal, fully concealed UL Classified smoke seals located within the head track assembly. Externally mounted smoke seals shall not be acceptable.
4. Counterbalance Unit: The fire door shall be counterbalanced by means of adjustable steel counterweight system that is to be located in an area as indicated in the construction drawings.
5. Electric Motor Operator: Fire door shall be provided with a compact power unit designed and built by the door manufacturer. Operator shall be equipped with an adjustable screw-type limit switch to break the circuit at termination of travel. High efficiency planetary gearing running in an oil bath, shall be furnished together with a centrifugal governor, magnetic operated brake and a fail-safe magnetic release device, completely housed to protect against damage, dust and moisture. An efficient overload protection device, which will break the power circuit and protect against damage to the motor windings shall be integral with the unit. Operator is to be housed in a NEMA type 1 enclosure.

1. Motor: Shall be intermediate duty, thermally protected, ball bearing type with a class A or better insulation. Horsepower of motor is to be 1/3hp minimum or of manufacturer's recommended size, which ever is greater.

2. Starter: Shall be size "0" magnetic reversing starter, across the line type with mechanical and electrical interlocks, with 10 amp continuous rating and 24 volt control circuit.

3. Reducer: Planetary gear type, 80% efficiency minimum.

4. Brake: Magnetically activated, integral within the operator's housing.

5. Control Station: Provide flush mount key switch control station marked open, close and stop.

1. Self-Closing Mechanism: The fire door is to be designed with a centrifugal governor as an integral part of the operator's construction. The automatic release mechanism shall be activated by smoke detector or fire alarm. When activated the door is released and begins to close due to the captured counterweight force. The speed of the door shall be governed by a centrifugal governor, designed to match the normal operating speed of the door, at a rate of not greater than 9" per second or less than 6" per second. The fire door shall self-close under its own power. Battery back-up systems to achieve self-closing are not acceptable.
2. Magnetic Release with 10 Second Time Delay: A fail-safe magnetic release device shall be built into the operator as an integral part of the release mechanism. When power is interrupted to the release mechanism by the smoke detector or fire alarm, the door shall begin to self-close. In the event of power failure the time delay shall prevent the fire door from closing for a period of 10 seconds. Once the 10 seconds have lapsed, the fire door shall self-close without the aid of electricity or battery back-up systems. Once power has been restored the automatic reset time delay as well as the fire door shall reset themselves.
3. Obstruction Sensing Device: The fire door shall be designed with a radio activated obstruction sensing safety edge. In the event that the safety edge meets an obstruction during the normal closing operation, the door shall stop, reverse and return to the open position. In the event the safety edge meets an obstruction during the self-closing operation, the door shall reverse and attempt to close three times. In the event that the obstruction has not been removed during the third attempt, the door shall come to rest on the obstruction and once the obstruction has been removed the fire door shall continue to the fully closed position.
4. Easy Trip Test Feature: The fire door shall be designed so that it may be trip tested simply by cutting power to the operator. By turning the power switch off, the door shall self-close. Once the fire door has satisfactorily closed, it shall be reset simply by turning the power back on. No ladders or tools shall be needed to reset the door or the time delay unit.
5. Finish: After completion of fabrication, clean all metal surfaces to remove dirt. All steel components shall receive two coats of rust inhibitive primer. All exposed stainless steel components shall be of type 304 with number 4 polish finish.

**PART 3 EXECUTION**

3.01 EXAMINATION

A. Examine surfaces and field conditions to which this work is to be performed and notify architect if conditions of surfaces exist which are detrimental to proper installation and timely completion of work.

B. Verify all dimensions taken at job site affecting the work. Notify the architect in any instance where dimensions vary.

C. Coordinate and schedule work under this section with work of other sections so as not to delay job progress.

3.02 INSTALLATION

A. Perform installation using only factory approved and certified representatives of the door manufacturer.

B. Install door assemblies at locations shown in perfect alignment and elevation, plumb, level, straight and true.

C. Adjust door installation to provide uniform clearances and smooth non-binding operation.

D. Install wiring in accordance with applicable local codes and the National Electrical Code Standard. Materials shall be UL listed.

E. Test door closing sequence when activated by the building's fire alarm system. Reset door after successful test.

3.03 PROTECTION AND CLEANING

A. Protect installed work using adequate and suitable means during and after installation until accepted by owner.

B. Remove, repair or replace materials which have been damaged in any way.

C. Clean surfaces of grime and dirt using acceptable and recommended means and methods.